## Bus index
Bus number | Node number | Relative weighting of demand within node | Wind trace name | Solar trace name | Bus numbers in original model | Peak in each state | Max demand
1 | 2 | 0 | Bubble SEN Wind 2014-2045_0910refyr.csv | CAN Solar PV.csv | 101 |  | 12979
2 | 2 | 0.116 | Bubble SEN Wind 2014-2045_0910refyr.csv | CAN Solar PV.csv | 102 | 15.0556
3 | 2 | 0 | Bubble HUN Wind 2014-2045_0910refyr.csv | Moree Solar.csv | 201
4 | 2 | 0 | Bubble WEN 2014-2045_0910refyr.csv | Nyngan.csv | 202
5 | 2 | 0 | Bubble NEN Wind 2014-2045_0910refyr.csv | NCEN Solar PV.csv | 203
6 | 2 | 0 | Bubble FWN 2014-2045_0910refyr.csv | SWNSW Solar Real PV.csv | 204
7 | 2 | 1.609 | Bubble HUN Wind 2014-2045_0910refyr.csv | NNS Solar PV.csv | 205 | 208.8321
8 | 2 | 1.345 | Bubble HUN Wind 2014-2045_0910refyr.csv | Moree Solar.csv | 206 | 174.5676
9 | 2 | 32.953 | Bubble NEN Wind 2014-2045_0910refyr.csv | NNS Solar PV.csv | 207 | 4276.9699
10 | 2 | 1.179 | Bubble NEN Wind 2014-2045_0910refyr.csv | NCEN Solar PV.csv | 208 | 153.0224
11 | 2 | 0 | Bubble WEN 2014-2045_0910refyr.csv | Nyngan.csv | 209
12 | 2 | 0 | Bubble WEN 2014-2045_0910refyr.csv | NCEN Solar PV.csv | 210
13 | 2 | 24.69 | Bubble HUN Wind 2014-2045_0910refyr.csv | NCEN Solar PV.csv | 211 | 3204.5151
14 | 2 | 16.22 | Bubble HUN Wind 2014-2045_0910refyr.csv | CAN Solar PV.csv | 212 | 2105.1938
15 | 2 | 0 | Bubble MRN Wind 2014-2045_0910refyr.csv | CAN Solar PV.csv | 213
16 | 2 | 0 | Bubble MRN Wind 2014-2045_0910refyr.csv | CAN Solar PV.csv | 214
17 | 2 | 0.905 | Bubble FWN 2014-2045_0910refyr.csv | SWNSW Solar Real PV.csv | 215 | 117.46
18 | 2 | 10.66 | Bubble FWN 2014-2045_0910refyr.csv | SWNSW Solar Real PV.csv | 216 | 1383.5614
19 | 2 | 10.323 | Bubble MUN Wind 2014-2045_0910refyr.csv | Broken Hill Solar Plant.csv | 217 | 1339.8222
20 | 3 | 0 | Bubble NWV Wind 2014-2045_0910refyr.csv | NVIC Solar PV.csv | 301 |  | 9355
21 | 3 | 0 | Bubble SEV Wind 2014-2045_0910refyr.csv | LV Solar Real PV.csv | 302
22 | 3 | 0 | Bubble NWV Wind 2014-2045_0910refyr.csv | NVIC Solar PV.csv | 303
23 | 3 | 0 | Bubble NWV Wind 2014-2045_0910refyr.csv | NVIC Solar PV.csv | 304
24 | 3 | 0 | Bubble SWV Wind 2014-2045_0910refyr.csv | CVIC Solar PV.csv | 305
25 | 3 | 37.71 | Bubble SWV Wind 2014-2045_0910refyr.csv | MEL Solar Real PV.csv | 306 | 3527.7705
26 | 3 | 8.85 | Bubble CS Wind 2014-2045_0910refyr.csv | MEL Solar Real PV.csv | 307 | 827.9175
27 | 3 | 8.95 | Bubble CS Wind 2014-2045_0910refyr.csv | MEL Solar Real PV.csv | 308 | 837.2725
28 | 3 | 3.79 | Bubble NWV Wind 2014-2045_0910refyr.csv | NVIC Solar PV.csv | 309 | 354.5545
29 | 3 | 0 | Bubble NWV Wind 2014-2045_0910refyr.csv | CVIC Solar PV.csv | 311
30 | 3 | 3.99 | Bubble SEV Wind 2014-2045_0910refyr.csv | LV Solar Real PV.csv | 312 | 373.2645
31 | 3 | 32.32 | Bubble SEV Wind 2014-2045_0910refyr.csv | LV Solar Real PV.csv | 313 | 3023.536
32 | 3 | 4.39 | Bubble SWV Wind 2014-2045_0910refyr.csv | CVIC Solar PV.csv | 314 | 410.6845
33 | 3 | 0 | Bubble CS Wind 2014-2045_0910refyr.csv | MEL Solar Real PV.csv | 315
34 | 4 | 0 | Bubble SWQ Wind 2014-2045_0910refyr.csv | CQ Solar PV.csv | 401 |  | 8644
35 | 4 | 0 | Bubble FNQ 2014-2045_0910refyr.csv | CQ Solar PV.csv | 402
36 | 4 | 0 | Bubble FNQ 2014-2045_0910refyr.csv | NQ Solar PV.csv | 403
37 | 4 | 0 | Bubble FNQ 2014-2045_0910refyr.csv | CQ Solar PV.csv | 404
38 | 4 | 17.39 | Bubble FNQ 2014-2045_0910refyr.csv | CQ Solar PV.csv | 405 | 1503.1916
39 | 4 | 16.43 | Bubble FNQ 2014-2045_0910refyr.csv | NQ Solar PV.csv | 406 | 1420.2092
40 | 4 | 0.58 | Bubble FNQ 2014-2045_0910refyr.csv | NQ Solar PV.csv | 407 | 50.1352
41 | 4 | 3.32 | Bubble FNQ 2014-2045_0910refyr.csv | CQ Solar PV.csv | 408 | 286.9808
42 | 4 | 5.78 | Bubble SWQ Wind 2014-2045_0910refyr.csv | CQ Solar PV.csv | 409 | 499.6232
43 | 4 | 5.77 | Bubble SWQ Wind 2014-2045_0910refyr.csv | CQ Solar PV.csv | 410 | 498.7588
44 | 4 | 33.98 | Bubble SWQ Wind 2014-2045_0910refyr.csv | SEQ Solar PV.csv | 411 | 2937.2312
45 | 4 | 16.75 | Bubble SWQ Wind 2014-2045_0910refyr.csv | SEQ Solar PV.csv | 412 | 1447.87
46 | 4 | 0 | Bubble SWQ Wind 2014-2045_0910refyr.csv | SWQ Solar PV.csv | 413
47 | 4 | 0 | Bubble SWQ Wind 2014-2045_0910refyr.csv | SWQ Solar PV.csv | 414
48 | 4 | 0 | Bubble SWQ Wind 2014-2045_0910refyr.csv | SWQ Solar PV.csv | 415
49 | 4 | 0 | Bubble SWQ Wind 2014-2045_0910refyr.csv | SWQ Solar PV.csv | 416
50 | 5 | 0 | Bubble MNS Wind 2014-2045_0910refyr.csv | NSA Solar PV.csv | 501 |  | 3110
51 | 5 | 0 | Bubble WCS Wind 2014-2045_0910refyr.csv | NSA Solar PV.csv | 502
52 | 5 | 0 | Bubble WCS Wind 2014-2045_0910refyr.csv | NSA Solar PV.csv | 503
53 | 5 | 8.606 | Bubble MNS Wind 2014-2045_0910refyr.csv | NSA Solar PV.csv | 504 | 267.6466
54 | 5 | 0 | Bubble WCS Wind 2014-2045_0910refyr.csv | NSA Solar PV.csv | 505
55 | 5 | 0 | Bubble WCS Wind 2014-2045_0910refyr.csv | NSA Solar PV.csv | 506
56 | 5 | 31.739 | Bubble MNS Wind 2014-2045_0910refyr.csv | NSA Solar PV.csv | 507 | 987.0829
57 | 5 | 49.702 | Bubble MNS Wind 2014-2045_0910refyr.csv | ADE Solar Real PV.csv | 508 | 1545.7322
58 | 5 | 9.953 | Bubble FLS Wind 2014-2045_0910refyr.csv | SESA Solar Real PV.csv | 509 | 309.5383

## Bus connections
From Index | To Index | Series reactance per line/tx (pu on 100 MVA) | Number of lines/tx's | Total MW limit | Generator connection (boolean) | MW Limit per line/tx | From Bus | To Bus | Line No. | R (pu on 100 MVA) | B (pu on 100 MVA) [shunt admittance] | Notes | MW Limit per line/tx
2 | 19 | 0.0667 | 2 | 1000 | 0 | 500 | 102 | 217 | 1,2 | 0.0084 | 0.817 | Serially compensated line merged with other line: bus 310 removed.
2 | 19 | 0.062 | 2 | 1000 | 0 | 500 | 102 | 217 | 3,4 | 0.0078 | 0.76 | Transformer
2 | 28 | 0.0356 | 2 | 1400 | 0 | 700 | 102 | 309 | 1,2 | 0.0045 | 0.437 | Transmission MW limits were developed to match generation and demand (they are not from any other source)
2 | 28 | 0.0868 | 1 | 700 | 0 | 700 | 102 | 309 | 3 | 0.0109 | 0.76
7 | 8 | 0.076 | 2 | 2000 | 0 | 1000 | 205 | 206 | 1,2 | 0.0096 | 0.931
7 | 49 | 0.046 | 2 | 1500 | 0 | 750 | 205 | 416 | 1,2 | 0.0037 | 0.73
8 | 9 | 0.0356 | 2 | 4600 | 0 | 2300 | 206 | 207 | 1,2 | 0.0045 | 0.437
8 | 14 | 0.0527 | 2 | 3000 | 0 | 1500 | 206 | 212 | 1,2 | 0.0066 | 0.646
8 | 17 | 0.0527 | 2 | 2000 | 0 | 1000 | 206 | 215 | 1,2 | 0.0066 | 0.646
9 | 10 | 0.014 | 2 | 4000 | 0 | 2000 | 207 | 208 | 1,2 | 0.0018 | 0.171
9 | 11 | 0.0062 | 1 | 2000 | 0 | 2000 | 207 | 209 | 1 | 0.0008 | 0.076
10 | 13 | 0.0248 | 3 | 4200 | 0 | 1400 | 208 | 211 | 1,2,3 | 0.0031 | 0.304
11 | 14 | 0.0356 | 1 | 1500 | 0 | 1500 | 209 | 212 | 1 | 0.0045 | 0.437
12 | 15 | 0.0145 | 2 | 3000 | 0 | 1500 | 210 | 213 | 1,2 | 0.001 | 1.54
13 | 14 | 0.0108 | 2 | 3000 | 0 | 1500 | 211 | 212 | 1,2 | 0.0014 | 0.133
13 | 16 | 0.0155 | 1 | 1000 | 0 | 1000 | 211 | 214 | 1 | 0.0019 | 0.19
14 | 19 | 0.0558 | 1 | 2000 | 0 | 2000 | 212 | 217 | 1 | 0.007 | 0.684
16 | 18 | 0.0077 | 1 | 2000 | 0 | 2000 | 214 | 216 | 1 | 0.001 | 0.095
16 | 19 | 0.0388 | 1 | 1000 | 0 | 1000 | 214 | 217 | 1 | 0.0049 | 0.475
17 | 18 | 0.0403 | 2 | 2000 | 0 | 1000 | 215 | 216 | 1,2 | 0.0051 | 0.494
17 | 19 | 0.0574 | 2 | 2000 | 0 | 1000 | 215 | 217 | 1,2 | 0.0072 | 0.703
18 | 19 | 0.0403 | 1 | 1000 | 0 | 1000 | 216 | 217 | 1 | 0.0051 | 0.494
22 | 23 | 0.014 | 1 | 1500 | 0 | 1500 | 303 | 304 | 1 | 0.001 | 1.48
22 | 24 | 0.016 | 2 | 2500 | 0 | 1250 | 303 | 305 | 1,2 | 0.0011 | 1.7
23 | 24 | 0.004 | 1 | 1000 | 0 | 1000 | 304 | 305 | 1 | 0.0003 | 0.424
24 | 25 | 0.003 | 1 | 2500 | 0 | 2500 | 305 | 306 | 1 | 0.0002 | 0.32
24 | 26 | 0.0045 | 2 | 2700 | 0 | 1350 | 305 | 307 | 1,2 | 0.0003 | 0.447
25 | 26 | 0.0012 | 1 | 2100 | 0 | 2100 | 306 | 307 | 1 | 0.0001 | 0.127
26 | 27 | 0.0325 | 2 | 2700 | 0 | 1350 | 307 | 308 | 1,2 | 0.0023 | 3.445
28 | 29 | 0.0376 | 2 | 2000 | 0 | 1000 | 309 | 311 | 1,2 | 0.009 | 0.874
30 | 31 | 0.015 | 1 | 5000 | 0 | 5000 | 312 | 313 | 1 | 0.002 | 0.9
31 | 32 | 0.005 | 1 | 1100 | 0 | 1100 | 313 | 314 | 1 | 0.0005 | 0.52
33 | 58 | 0.05 | 2 | 2700 | 0 | 1350 | 315 | 509 | 1,2 | 0.007 | 0.19
38 | 39 | 0.0475 | 2 | 1500 | 0 | 750 | 405 | 406 | 1,2 | 0.0039 | 0.381
38 | 41 | 0.05 | 1 | 1000 | 0 | 1000 | 405 | 408 | 1 | 0.0054 | 0.189
38 | 42 | 0.122 | 3 | 2400 | 0 | 800 | 405 | 409 | 1,2,3 | 0.018 | 0.790 *
39 | 40 | 0.0076 | 2 | 1000 | 0 | 500 | 406 | 407 | 1,2 | 0.0006 | 0.062
40 | 41 | 0.0513 | 1 | 1000 | 0 | 1000 | 407 | 408 | 1 | 0.0042 | 0.412
41 | 43 | 0.128 | 2 | 2000 | 0 | 1000 | 408 | 410 | 1,2 | 0.011 | 1.01
42 | 44 | 0.0709 | 2 | 2600 | 0 | 1300 | 409 | 411 | 1,2 | 0.0103 | 0.46
43 | 44 | 0.0532 | 1 | 1500 | 0 | 1500 | 410 | 411 | 1 | 0.0043 | 0.427
43 | 45 | 0.0532 | 4 | 3600 | 0 | 900 | 410 | 412 | 1,2,3,4 | 0.0043 | 0.427
43 | 46 | 0.0494 | 2 | 1500 | 0 | 750 | 410 | 413 | 1,2 | 0.004 | 0.4
44 | 45 | 0.0152 | 2 | 2400 | 0 | 1200 | 411 | 412 | 1,2 | 0.0012 | 0.122
47 | 48 | 0.025 | 2 | 1500 | 0 | 750 | 414 | 415 | 1,2 | 0.002 | 0.39
48 | 49 | 0.046 | 2 | 1500 | 0 | 750 | 415 | 416 | 1,2 | 0.0037 | 0.73
53 | 56 | 0.15 | 2 | 1000 | 0 | 500 | 504 | 507 | 1,2 | 0.023 | 0.56
53 | 57 | 0.019 | 2 | 600 | 0 | 300 | 504 | 508 | 1,2 | 0.026 | 0.87
54 | 56 | 0.0085 | 1 | 1100 | 0 | 1100 | 505 | 507 | 1 | 0.0008 | 0.06
54 | 57 | 0.028 | 1 | 1500 | 0 | 1500 | 505 | 508 | 1 | 0.0025 | 0.17
55 | 56 | 0.0085 | 1 | 600 | 0 | 600 | 506 | 507 | 1 | 0.0008 | 0.06
55 | 57 | 0.028 | 1 | 600 | 0 | 600 | 506 | 508 | 1 | 0.003 | 0.14
56 | 57 | 0.019 | 1 | 1500 | 0 | 1500 | 507 | 508 | 1 | 0.002 | 0.09
56 | 58 | 0.22 | 2 | 2500 | 0 | 1250 | 507 | 509 | 1,2 | 0.03 | 0.9
1 | 2 | 0.036 | 1 | 333.3 | 1 | 333.3 | 101 | 102
3 | 8 | 0.024 | 1 | 666.7 | 1 | 666.7 | 201 | 206
4 | 11 | 0.0288 | 1 | 555.6 | 1 | 555.6 | 202 | 209
5 | 10 | 0.0306 | 1 | 555.6 | 1 | 555.6 | 203 | 208
6 | 17 | 0.024 | 1 | 666.7 | 1 | 666.7 | 204 | 215
11 | 12 | 0.0272 | 4 | 3000 | 0 | 750 | 209 | 210
15 | 16 | 0.0272 | 4 | 3000 | 0 | 750 | 213 | 214
20 | 22 | 0.024 | 1 | 666.7 | 1 | 666.7 | 301 | 303
21 | 30 | 0.0338 | 1 | 444.4 | 1 | 444.4 | 302 | 312
23 | 31 | 0.032 | 2 | 1000 | 0 | 500 | 304 | 313
24 | 29 | 0.024 | 2 | 2000 | 0 | 1000 | 305 | 311
24 | 32 | 0.0243 | 2 | 1000 | 0 | 500 | 305 | 314
27 | 33 | 0.027 | 2 | 2500 | 0 | 1250 | 308 | 315
34 | 43 | 0.0338 | 1 | 444.4 | 1 | 444.4 | 401 | 410
35 | 41 | 0.051 | 1 | 333.3 | 1 | 333.3 | 402 | 408
36 | 40 | 0.0338 | 1 | 444.4 | 1 | 444.4 | 403 | 407
37 | 38 | 0.051 | 1 | 333.3 | 1 | 333.3 | 404 | 405
46 | 47 | 0.008 | 2 | 1500 | 0 | 750 | 413 | 414
50 | 53 | 0.051 | 1 | 333.3 | 1 | 333.3 | 501 | 504
51 | 54 | 0.064 | 1 | 250 | 1 | 250 | 502 | 505
52 | 55 | 0.1 | 1 | 166.7 | 1 | 166.7 | 503 | 506

## Node index
Node number | Demand Trace | Relative weighting of PV within node | PV names | PV colours | Notes
2 | 2014 NSW1 Medium 10POE_0910refyr.csv | 0.2555 | Rooftop PV NSW | Moccasin | NSW & CAN
3 | 2014 VIC1 Medium 10POE_0910refyr.csv | 0.2111 | Rooftop PV VIC | Khaki | VIC
4 | 2014 QLD1 Medium 10POE_0910refyr.csv | 0.3698 | Rooftop PV QLD | Yellow | QLD
5 | 2014 SA1 Medium 10POE_0910refyr.csv | 0.1636 | Rooftop PV SA | Gold | SA
For this example, use 4102 MW PV capacity
Nodes are numbered starting at 2 to match the original bus numbering system in the 58-bus model

## Generator data
Name | Colour name | Bus number | Type (numeric key) | Max output (MW) | Min output (MW) | Ramp up (MW/hr) | Ramp down (MW/hr) | Start cost ($) | Shut cost ($) | SRMC ($/MWh) | Min up time (hr) | Min down time (hr) | Storage (MWh) | CSP & utility storage max charge/discharge rate (MW) | Utility storage min charge/discharge rate (MW) | Utility storage charging ramp up (MW/hr) | Utility storage charging ramp down (MW/hr) | Utility storage efficiency | CSP & PV solar multiple
Brown coal LV | SaddleBrown | 21 | 1 | 4992 | 3183 | 2860 | 2940 | 1050 | 0 | 7.14 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Brown coal NSA | Sienna | 50 | 1 | 650 | 345 | 410 | 410 | 700 | 0 | 25.61 | 16 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Black coal CQ | DarkSlateGray | 35 | 2 | 4567 | 2116 | 2430 | 2570 | 1400 | 0 | 25.31 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Black coal NNS | MidnightBlue | 3 | 2 | 3320 | 1594 | 720 | 600 | 700 | 0 | 30.44 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Black coal CAN | Black | 4 | 2 | 2880 | 922 | 600 | 600 | 350 | 0 | 29.78 | 8 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CCGT CQ | LightGrey | 37 | 3 | 1556 | 311.2 | 4543.52 | 4341.24 | 100 | 0 | 38.45 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CCGT SESA | Silver | 52 | 3 | 678 | 68 | 1540 | 1540 | 50 | 0 | 41.85 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CCGT NCEN | DarkGray | 5 | 3 | 2231 | 223.1 | 1896.35 | 2208.69 | 50 | 0 | 47.62 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CCGT CVIC | SlateGray | 24 | 3 | 1000 | 100 | 800 | 800 | 90 | 0 | 54.13 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OCGT MEL | Violet | 20 | 4 | 2362 | 236 | 34715 | 13335 | 700 | 0 | 86.34 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OCGT SWQ | Fuchsia | 34 | 4 | 3479 | 348 | 7380 | 7410 | 400 | 0 | 90.51 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OCGT ADE | MediumOrchid | 51 | 4 | 2131 | 213 | 15790 | 14600 | 800 | 0 | 93.95 | 4 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0
OCGT SWNSW | DarkViolet | 6 | 4 | 3700 | 370 | 5520 | 5520 | 200 | 0 | 97.97 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Utility Storage NNS | LightBlue | 8 | 6 | 2000 | 20 | 1200 | 1200 | 0 | 0 | 0 | 0 | 0 | 12000 | 1800 | 20 | 630 | 630 | 0.85 | 0
Utility Storage NCEN | Aqua | 13 | 6 | 1500 | 15 | 900 | 900 | 0 | 0 | 0 | 0 | 0 | 9000 | 1350 | 15 | 472.5 | 472.5 | 0.85 | 0
Utility Storage CAN | CornflowerBlue | 11 | 6 | 1000 | 10 | 600 | 600 | 0 | 0 | 0 | 0 | 0 | 6000 | 900 | 10 | 315 | 315 | 0.85 | 0
Utility Storage MEL | LightSkyBlue | 25 | 6 | 1500 | 15 | 900 | 900 | 0 | 0 | 0 | 0 | 0 | 9000 | 1350 | 15 | 472.5 | 472.5 | 0.85 | 0
Utility Storage LV | DeepSkyBlue | 31 | 6 | 1500 | 15 | 900 | 900 | 0 | 0 | 0 | 0 | 0 | 9000 | 1350 | 15 | 472.5 | 472.5 | 0.85 | 0
Utility Storage CQ | DodgerBlue | 38 | 6 | 750 | 7.5 | 450 | 450 | 0 | 0 | 0 | 0 | 0 | 4500 | 675 | 7.5 | 236.25 | 236.25 | 0.85 | 0
Utility Storage SWQ | RoyalBlue | 45 | 6 | 1500 | 15 | 900 | 900 | 0 | 0 | 0 | 0 | 0 | 9000 | 1350 | 15 | 472.5 | 472.5 | 0.85 | 0
Utility Storage SESA | Blue | 57 | 6 | 750 | 7.5 | 450 | 450 | 0 | 0 | 0 | 0 | 0 | 4500 | 675 | 7.5 | 236.25 | 236.25 | 0.85 | 0
Wind NNS | PaleGreen | 9 | 7 | 2500 | 10 | 2500 | 2500 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind SWNSW | LimeGreen | 19 | 7 | 2500 | 10 | 2500 | 2500 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind MEL | Lime | 26 | 7 | 2500 | 10 | 2500 | 2500 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind NVIC | GreenYellow | 28 | 7 | 2500 | 10 | 2500 | 2500 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind NQ | YellowGreen | 36 | 7 | 2500 | 10 | 2500 | 2500 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind SEQ | MediumSeaGreen | 44 | 7 | 2500 | 10 | 2500 | 2500 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind NSA | ForestGreen | 56 | 7 | 2500 | 10 | 2500 | 2500 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Wind SESA | DarkGreen | 58 | 7 | 2552 | 10 | 2552 | 2552 | 0 | 0 | 3.86 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Utility PV CQ | Orange | 42 | 8 | 1000 | 10 | 1000 | 1000 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
Utility PV CAN | OrangeRed | 14 | 8 | 1000 | 10 | 1000 | 1000 | 0 | 0 | 2.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1